## Client Modbus TCP API
xStorage XV Application controller Modbus TCP map
Address range | Description |  |  | Protocol: Modbus TCP
0-99 | Control + summary values for the whole system |  |  | XV = Modbus master,client/Netbiter = Modbus slave
600-799 | Parameters |  |  | Ethernet port #2
7600-7800 | EM20 Power meter
PCS/Battery data, like in SC-XV table, but with offset of 1000 |  |  |  | Preference that whole block is sent cyclically, >=500ms from Ext
OFFSET: PCS 0 = 1000, PCS 1 = 2000, PCS 2 = 3000, PCS 3 = 4000, PCS 4 = 5000 |  |  |  | All data is big-endian
200-299 | Battery string 0 details
300-399 | Battery string 1 details
400-499 | Battery string 2 details
500-599 | PCS details
i.e. : PCS3 Battery string 2 = 4400 - >
Power meter values = EM20 power meter modbus table
Modbus Address | Word count | Signal Name | Valid Range | Unit | Scaling | Register Type | Datatype | Description
7688 | 1 | Phase 1 Amps | "-32768...32767" | - | 100 | Input (FC04) | INT16
7689 | 1 | Phase 2 Amps | "-32768...32767" | - | 100 | Input (FC04) | INT16
7690 | 1 | Phase 3 Amps | "-32768...32767" | - | 100 | Input (FC04) | INT16
7691 | 1 | Phase 1 Volts | 0-65553 | V | 10 | Input (FC04) | UINT16
7692 | 1 | Phase 2 Volts | 0-65553 | V | 10 | Input (FC04) | UINT16
7693 | 1 | Phase 3 Volts | 0-65553 | V | 10 | Input (FC04) | UINT16
7694 | 1 | Ph1-Ph2 Volts | 0-65553 | V | 10 | Input (FC04) | UINT16
7695 | 1 | Ph2-Ph3 Volts | 0-65553 | V | 10 | Input (FC04) | UINT16
7696 | 1 | Ph3-Ph1 Volts | 0-65553 | V | 10 | Input (FC04) | UINT16
7697 | 1 | Frequency | 0-65553 | Hz | 1000 | Input (FC04) | UINT16
7698 | 1 | Phase 1 PF | 0-65553 |  | 1000 | Input (FC04) | UINT16
7699 | 1 | Phase 2 PF | 0-65553 |  | 1000 | Input (FC04) | UINT16
7700 | 1 | Phase 3 PF | 0-65553 |  | 1000 | Input (FC04) | UINT16
7701 | 1 | System PF | 0-65553 |  | 1000 | Input (FC04) | UINT16
7702 | 1 | Phase 1 kW | "-32768...32767" | - | 100 | Input (FC04) | INT16
7703 | 1 | Phase 2 kW | "-32768...32767" | - | 100 | Input (FC04) | INT16
7704 | 1 | Phase 3 kW | "-32768...32767" | - | 100 | Input (FC04) | INT16
7705 | 1 | System kW | "-32768...32767" | - | 100 | Input (FC04) | INT16
7706 | 1 | Phase 1 kVA | "-32768...32767" | - | 100 | Input (FC04) | INT16
7707 | 1 | Phase 2 kVA | "-32768...32767" | - | 100 | Input (FC04) | INT16
7708 | 1 | Phase 3 kVA | "-32768...32767" | - | 100 | Input (FC04) | INT16
7709 | 1 | System kVA | "-32768...32767" | - | 100 | Input (FC04) | INT16
7710 | 1 | Phase 1 kvar | "-32768...32767" | - | 100 | Input (FC04) | INT16
7711 | 1 | Phase 2 kvar | "-32768...32767" | - | 100 | Input (FC04) | INT16
7712 | 1 | Phase 3 kvar | "-32768...32767" | - | 100 | Input (FC04) | INT16
7713 | 1 | System kvar | "-32768...32767" | - | 100 | Input (FC04) | INT16
Grid code related parameters
Modbus Address | Word count | Signal Name | Valid Range | Unit | Scaling | Register Type | Datatype | Description
600 | 1 | Year | 0-65553 | y | 1 | Holding (FC03) | UINT16
601 | 1 | Month | 1-12 | min | 1 | Holding (FC03) | UINT16
602 | 1 | Day | 1-31 | d | 1 | Holding (FC03) | UINT16
603 | 1 | Hours | 0-23 | h | 1 | Holding (FC03) | UINT16
604 | 1 | Minutes | 0-59 | min | 1 | Holding (FC03) | UINT16
605 | 1 | Seconds | 0-59 | s | 1 | Holding (FC03) | UINT16
606 | 1 | Set time | 0-1 | - | 1 | Holding (FC03) | UINT16
607 | 1 | Param18 | 0-65553 | - | - | Holding (FC03) | UINT16
608 | 1 | Param19 | 0-65553 | - | - | Holding (FC03) | UINT16
609 | 1 | Param20 | 0-65553 | - | - | Holding (FC03) | UINT16
610 | 1 | Auto control ON/OFF(use scheduler) | 0-1 | - | 1 | Holding (FC03) | UINT16
611 | 1 | Program 1 ON/OFF(Zero input) | 0-1 | - | 1 | Holding (FC03) | UINT16
612 | 1 | Program 2 ON/OFF(Zero feed) | 0-1 | - | 1 | Holding (FC03) | UINT16
613 | 1 | Program 3 ON/OFF(x) | 0-1 | - | 1 | Holding (FC03) | UINT16
614 | 1 | Timer default max charge | 0-200 | kW | 10 | Holding (FC03) | UINT16
615 | 1 | Timer default max discharge | 0-200 | kW | 10 | Holding (FC03) | UINT16
616 | 1 | Timer default max Input kW | 0-200 | kW | 10 | Holding (FC03) | UINT16
617 | 1 | Timer default min SoC | 0-100 | % | 1 | Holding (FC03) | UINT16
618 | 1 | Timer default max Soc | 0-100 | % | 1 | Holding (FC03) | UINT16
619 | 1 | Timer default Control mode | 0-100 | - | 1 | Holding (FC03) | UINT16
620 | 1 | Timer 0 Day on | 0-6 | weekday | 1 | Holding (FC03) | UINT16 | Mo-Su
621 | 1 | Timer 0 Day off | 0-6 | weekday | 1 | Holding (FC03) | UINT16 | Mo-Su
622 | 1 | Timer 0 Hour On | 0-23 | h | 1 | Holding (FC03) | UINT16
623 | 1 | Timer 0 Hour Off | 0-23 | h | 1 | Holding (FC03) | UINT16
624 | 1 | Timer 0 Minute On | 0-59 | min | 1 | Holding (FC03) | UINT16
625 | 1 | Timer 0 Minute Off | 0-59 | min | 1 | Holding (FC03) | UINT16
626 | 1 | Timer 0 Max charge kW | 0-200 | kW | 10 | Holding (FC03) | UINT16
627 | 1 | Timer 0 max discharge | 0-200 | kW | 10 | Holding (FC03) | UINT16
628 | 1 | Timer 0 max Input kW | 0-200 | kW | 10 | Holding (FC03) | UINT16
629 | 1 | Timer 0 min SoC | 0-100 | % | 1 | Holding (FC03) | UINT16
630 | 1 | Timer 0 max Soc | 0-100 | % | 1 | Holding (FC03) | UINT16
631 | 1 | Timer 0 Power meter offset | "-200...200" | kW | 10 | Holding (FC03) | UINT16
632 | 1 | Timer 0 Control mode | 0-100 | - | 1 | Holding (FC03) | UINT16
633 | 1 | Timer 1 Day on | 0-6 | weekday | 1 | Holding (FC03) | UINT16 | Mo-Su
634 | 1 | Timer 1 Day off | 0-6 | weekday | 1 | Holding (FC03) | UINT16 | Mo-Su
635 | 1 | Timer 1 Hour On | 0-23 | h | 1 | Holding (FC03) | UINT16
636 | 1 | Timer 1 Hour Off | 0-23 | h | 1 | Holding (FC03) | UINT16
637 | 1 | Timer 1 Minute On | 0-59 | min | 1 | Holding (FC03) | UINT16
638 | 1 | Timer 1 Minute Off | 0-59 | min | 1 | Holding (FC03) | UINT16
639 | 1 | Timer 1 Max charge kW | 0-200 | kW | 10 | Holding (FC03) | UINT16
640 | 1 | Timer 1 max discharge | 0-200 | kW | 10 | Holding (FC03) | UINT16
641 | 1 | Timer 1 max Input kW | 0-200 | kW | 10 | Holding (FC03) | UINT16
642 | 1 | Timer 1 min SoC | 0-100 | % | 1 | Holding (FC03) | UINT16
643 | 1 | Timer 1 max Soc | 0-100 | % | 1 | Holding (FC03) | UINT16
644 | 1 | Timer 1 Power meter offset | "-200...200" | kW | 10 | Holding (FC03) | UINT16
645 | 1 | Timer 1 Control mode | 0-100 | - | 1 | Holding (FC03) | UINT16
646 | 1 | Timer 2 Day on | 0-6 | weekday | 1 | Holding (FC03) | UINT16 | Mo-Su
647 | 1 | Timer 2 Day off | 0-6 | weekday | 1 | Holding (FC03) | UINT16 | Mo-Su
648 | 1 | Timer 2 Hour On | 0-23 | h | 1 | Holding (FC03) | UINT16
649 | 1 | Timer 2 Hour Off | 0-23 | h | 1 | Holding (FC03) | UINT16
650 | 1 | Timer 2 Minute On | 0-59 | min | 1 | Holding (FC03) | UINT16
651 | 1 | Timer 2 Minute Off | 0-59 | min | 1 | Holding (FC03) | UINT16
652 | 1 | Timer 2 Max charge kW | 0-200 | kW | 10 | Holding (FC03) | UINT16
653 | 1 | Timer 2 max discharge | 0-200 | kW | 10 | Holding (FC03) | UINT16
654 | 1 | Timer 2 max Input kW | 0-200 | kW | 10 | Holding (FC03) | UINT16
655 | 1 | Timer 2 min SoC | 0-100 | % | 1 | Holding (FC03) | UINT16
656 | 1 | Timer 2 max Soc | 0-100 | % | 1 | Holding (FC03) | UINT16
657 | 1 | Timer 2 Power meter offset | "-200...200" | kW | 10 | Holding (FC03) | INT16
658 | 1 | Timer 2 Control mode | 0-100 | - | 1 | Holding (FC03) | UINT16
659 | 1 | Timer 3 Day on | 0-6 | weekday | 1 | Holding (FC03) | UINT16 | Mo-Su
660 | 1 | Timer 3 Day off | 0-6 | weekday | 1 | Holding (FC03) | UINT16 | Mo-Su
661 | 1 | Timer 3 Hour On | 0-23 | h | 1 | Holding (FC03) | UINT16
662 | 1 | Timer 3 Hour Off | 0-23 | h | 1 | Holding (FC03) | UINT16
663 | 1 | Timer 3 Minute On | 0-59 | min | 1 | Holding (FC03) | UINT16
664 | 1 | Timer 3 Minute Off | 0-59 | min | 1 | Holding (FC03) | UINT16
665 | 1 | Timer 3 Max charge kW | 0-200 | kW | 10 | Holding (FC03) | UINT16
666 | 1 | Timer 3 max discharge | 0-200 | kW | 10 | Holding (FC03) | UINT16
667 | 1 | Timer 3 max Input kW | 0-200 | kW | 10 | Holding (FC03) | UINT16
668 | 1 | Timer 3 min SoC | 0-100 | % | 1 | Holding (FC03) | UINT16
669 | 1 | Timer 3 max Soc | 0-100 | % | 1 | Holding (FC03) | UINT16
670 | 1 | Timer 3 Power meter offset | "-200...200" | kW | 10 | Holding (FC03) | INT16
671 | 1 | Timer 3 Control mode | 0-100 | - | 1 | Holding (FC03) | UINT16
672 | 1 | Timer 4 Day on | 0-6 | weekday | 1 | Holding (FC03) | UINT16 | Mo-Su
673 | 1 | Timer 4 Day off | 0-6 | weekday | 1 | Holding (FC03) | UINT16 | Mo-Su
674 | 1 | Timer 4 Hour On | 0-23 | h | 1 | Holding (FC03) | UINT16
675 | 1 | Timer 4 Hour Off | 0-23 | h | 1 | Holding (FC03) | UINT16
676 | 1 | Timer 4 Minute On | 0-59 | min | 1 | Holding (FC03) | UINT16
677 | 1 | Timer 4 Minute Off | 0-59 | min | 1 | Holding (FC03) | UINT16
678 | 1 | Timer 4 Max charge kW | 0-200 | kW | 10 | Holding (FC03) | UINT16
679 | 1 | Timer 4 max discharge | 0-200 | kW | 10 | Holding (FC03) | UINT16
680 | 1 | Timer 4 max Input kW | 0-200 | kW | 10 | Holding (FC03) | UINT16
681 | 1 | Timer 4 min SoC | 0-100 | % | 1 | Holding (FC03) | UINT16
682 | 1 | Timer 4 max Soc | 0-100 | % | 1 | Holding (FC03) | UINT16
683 | 1 | Timer 4 Power meter offset | "-200...200" | kW | 10 | Holding (FC03) | UINT16
684 | 1 | Timer 4 Control mode | 0-100 | - | 1 | Holding (FC03) | UINT16
685 | 1 | Timer 5 Day on | 0-6 | weekday | 1 | Holding (FC03) | UINT16 | Mo-Su
686 | 1 | Timer 5 Day off | 0-6 | weekday | 1 | Holding (FC03) | UINT16 | Mo-Su
687 | 1 | Timer 5 Hour On | 0-23 | h | 1 | Holding (FC03) | UINT16
688 | 1 | Timer 5 Hour Off | 0-23 | h | 1 | Holding (FC03) | UINT16
689 | 1 | Timer 5 Minute On | 0-59 | min | 1 | Holding (FC03) | UINT16
690 | 1 | Timer 5 Minute Off | 0-59 | min | 1 | Holding (FC03) | UINT16
691 | 1 | Timer 5 Max charge kW | 0-200 | kW | 10 | Holding (FC03) | UINT16
692 | 1 | Timer 5 max discharge | 0-200 | kW | 10 | Holding (FC03) | UINT16
693 | 1 | Timer 5 max Input kW | 0-200 | kW | 10 | Holding (FC03) | UINT16
694 | 1 | Timer 5 min SoC | 0-100 | % | 1 | Holding (FC03) | UINT16
695 | 1 | Timer 5 max Soc | 0-100 | % | 1 | Holding (FC03) | UINT16
696 | 1 | Timer 5 Power meter offset | "-200...200" | kW | 10 | Holding (FC03) | UINT16
697 | 1 | Timer 5 Control mode | 0-100 | - | 1 | Holding (FC03) | UINT16
698 | 1 | Timer 6 Day on | 0-6 | weekday | 1 | Holding (FC03) | UINT16 | Mo-Su
699 | 1 | Timer 6 Day off | 0-6 | weekday | 1 | Holding (FC03) | UINT16 | Mo-Su
700 | 1 | Timer 6 Hour On | 0-23 | h | 1 | Holding (FC03) | UINT16
701 | 1 | Timer 6 Hour Off | 0-23 | h | 1 | Holding (FC03) | UINT16
702 | 1 | Timer 6 Minute On | 0-59 | min | 1 | Holding (FC03) | UINT16
703 | 1 | Timer 6 Minute Off | 0-59 | min | 1 | Holding (FC03) | UINT16
704 | 1 | Timer 6 Max charge kW | 0-200 | kW | 10 | Holding (FC03) | UINT16
705 | 1 | Timer 6 max discharge | 0-200 | kW | 10 | Holding (FC03) | UINT16
706 | 1 | Timer 6 max Input kW | 0-200 | kW | 10 | Holding (FC03) | UINT16
707 | 1 | Timer 6 min SoC | 0-100 | % | 1 | Holding (FC03) | UINT16
708 | 1 | Timer 6 max Soc | 0-100 | % | 1 | Holding (FC03) | UINT16
709 | 1 | Timer 6 Power meter offset | "-200...200" | kW | 10 | Holding (FC03) | UINT16
710 | 1 | Timer 6 Control mode | 0-100 | - | 1 | Holding (FC03) | UINT16
OFFSET: PCS 0 = 1000, PCS 1 = 2000, PCS 2 = 3000, PCS 3 = 4000, PCS 4 = 5000
Modbus Address | Word count | Signal Name | Valid Range | Unit | Scaling | Register Type | Datatype | Description
0 | 1 | System Status | 0-1000 | - | - | Holding (FC03) | UINT16 | See details #1 below
1 | 2 | Power Request (active Power) (Big-Endian) | -1000000…1000000 | W | 1 | Holding (FC03) | INT32 | Power setpoint. By default, positive is discharging and negative charging.
3 | 2 | Power Request (reactive Power) (Big-Endian) | -1000000…1000000 | Var | 1 | Holding (FC03) | INT32 | (not implemented)
5 | 1 | Ext Error | 0=no Error, 1=Error | - | - | Holding (FC03) | UINT16 | Error in external contol unit. Not used for now - you can write what you want into this register.
6 | 1 | General Error Reset | trigger on flank | - | - | Holding (FC03) | UINT16 | Error reset of ESS error. Writing 1 into this register will ack the current "Storage System Error", possibly displaying a new one or eventually the same if same fault condition is still present/occurs again.
7 | 1 | Alive Counter | 0-65553 | - | - | Holding (FC03) | UINT16 | Alive value, upcounting, to check if connection is alive, counting up until 65535 and restarts with 0. If no write request is received for a given amount of time (indenpendently of the register / registers ESS writes into) system is put to idle. External controller should write the whole range of the registers at once, at a rate of maximum twice a second. If you choose to write something into this register, writing at least twice the same value consecutively will start a timeout. If the timeout expires, the system will be put into idle. Writing another new value will stop and reset it.
8 | 1 | Max input power | 0-65535 | W | 1 | Holding (FC03) | UINT16
Summary values
Modbus Address | Word count | Signal Name | Valid Range | Unit | Scaling | Register Type | Datatype | Description
0 | 1 | System Status | 0-1000 | - | - | Input (FC04) | UINT16 | See details #2 below
1 | 1 | Error bits | - | - | - | Input (FC04) | BITFIELD | See details #3 below
Modbus Address | Word count | Signal Name | Valid Range | Unit | Scaling | Register Type | Datatype | Description
2 | 2 | Battery Current | 0-2000 | - | 100 | Input (FC04) | INT32 | Sum of absolute current flowing into connected strings
4 | 2 | Current mesured active power | -1000000…1000000 | W | 1 | Input (FC04) | INT32
6 | 2 | Current measured reactive power | -1000000…1000000 | Var | 1 | Input (FC04) | INT32
8 | 1 | State of Charge | 0…100 | 1% | 1 | Input (FC04) | UINT8
9 | 1 | Alive Counter | 0-65553 | - | - | Input (FC04) | UINT16 | Alive value, upcounting, for Ext to check if connection is alive, counting up until 65535 and restarts with 0. System uses two separate counters (Ext increases own counter, ESS increases own counter)
10 | 2 | Maximum available power charge | 0…10000000 | W | 1 | Input (FC04) | INT32 | Maximum charging power capability. Reference point at inverter AC terminals
12 | 2 | Maximum available power discharge | 0…10000000 | W | 1 | Input (FC04) | INT32 | Maximum discharging power capability. Reference point at inverter AC terminals
14 | 1 | Storage System Error | Error Code | - | - | Input (FC04) | UINT16 | See details #4 below
15 | 2 | Battery bank capacity | 0....100E6 | Wh | 1 | Input (FC04) | UINT32 | Energy in battery (last 3 digits insignificant)
17 | 2 | Energy available to discharge (total availale energy) | 0....100E6 | Wh | 1 | Input (FC04) | UINT32 | Value given at full (rated) system power
19 | 2 | Energy available to charge (total available energy) | 0....100E6 | Wh | 1 | Input (FC04) | UINT32 | Value given at full (rated) system power
21 | 2 | Discharging energy reserved for other users | 0....100E6 | Wh | 1 | Input (FC04) | UINT32 | Value given at full (rated) system power
23 | 2 | Charging energy reserved for other users | 0....100E6 | Wh | 1 | Input (FC04) | UINT32 | Value given at full (rated) system power
25 | 32 | Unique ID | - | - | - | Input (FC04) | String(64) | XXX-NN-nnnnnnnn (Site ID - number - PCS serial number)
57 | 1 | Battery bank voltage (average voltage of all connected strings) | 0-65553 | V | 10 | Input (FC04) | UINT16
58 | 1 | Maximum cell voltage of the present strings | 0-65553 | mV | 1 | Input (FC04) | UINT16
59 | 1 | Minimum cell voltage of the present strings | 0-65553 | mV | 1 | Input (FC04) | UINT16
60 | 1 | ID of the string with max cell voltage | 0-65553 | - | - | Input (FC04) | UINT16
61 | 1 | ID of the string with min cell voltage | 0-65553 | - | - | Input (FC04) | UINT16
62 | 1 | ID of the pack with max cell voltage | 0-65553 | - | - | Input (FC04) | UINT16
63 | 1 | ID of the pack with min cell voltage | 0-65553 | - | - | Input (FC04) | UINT16
64 | 1 | Maximum cell temperature of the present strings | "-32768...32767" | °C | 10 | Input (FC04) | INT16
65 | 1 | Minimum cell temperature of the present strings | "-32768...32767" | °C | 10 | Input (FC04) | INT16
66 | 1 | ID of the string with max cell temp | 0-65553 | - | - | Input (FC04) | UINT16
67 | 1 | ID of the string with min cell temp | 0-65553 | - | - | Input (FC04) | UINT16
68 | 1 | ID of the pack with max cell temp | 0-65553 | - | - | Input (FC04) | UINT16
69 | 1 | ID of the pack with min cell temp | 0-65553 | - | - | Input (FC04) | UINT16
70 | 1 | Minimum current of the connected strings | 0-65553 | A | 100 | Input (FC04) | INT16
71 | 1 | Maximum current of the connected strings | 0-65553 | A | 100 | Input (FC04) | INT16
72 | 1 | ID of the string with the minimum current | 0-65553 | - | - | Input (FC04) | UINT16
73 | 1 | ID of the string with the maximum current | 0-65553 | - | - | Input (FC04) | UINT16
74 | 1 | Minimum chargeable current of the connected strings | 0-65553 | A | 100 | Input (FC04) | UINT16
75 | 1 | Maximum chargeable current of the connected strings | 0-65553 | A | 100 | Input (FC04) | UINT16
76 | 1 | ID of the string with the minimum chargeable current | 0-65553 | - | - | Input (FC04) | UINT16
77 | 1 | ID of the string with the maximum chargeable current | 0-65553 | - | - | Input (FC04) | UINT16
78 | 2 | Actual set converter power (with regulation if enabled) | -1000000…1000000 | W | 1 | Input (FC04) | INT32
80 | 1 | Grid frequency | 0-65553 | Hz | 100 | Input (FC04) | UINT16
81 | 1 | Converter ambiant temperature | 0-65553 | °C | 10 | Input (FC04) | UINT16
82 | 1 | Amount of strings configured | 1…54 | - | - | Input (FC04) | UINT16
83 | 1 | Status of string 0 | 0...3 | - | - | Input (FC04) | UINT16 | 0 = OFFLINE, 1= DETECTING, 2= AVAILABLE, 3= ONLINE
84 | 1 | Status of string 1 | 0...3 | - | - | Input (FC04) | UINT16 | 0 = OFFLINE, 1= DETECTING, 2= AVAILABLE, 3= ONLINE
85 | 1 | Status of string 2 | 0...3 | - | - | Input (FC04) | UINT16 | 0 = OFFLINE, 1= DETECTING, 2= AVAILABLE, 3= ONLINE
BMS detailed data
Modbus Address | Word count | Signal Name | Valid Range | Unit | Scaling | Register Type | Datatype | Description
|  | String 0 | [5 empty] | String IDs = 0x60, 0x01,0x02,0x03,0x04
200 | 1 | Total voltage | 0-65553 | V | 10 | Input (FC04) | UINT16
201 | 1 | Current | "-32768...32767" | - | 100 | Input (FC04) | INT16
202 | 1 | Max temp | "-32768...32767" | °C | 10 | Input (FC04) | INT16
203 | 1 | Min temp | "-32768...32767" | °C | 10 | Input (FC04) | INT16
204 | 1 | Max Cell V | 0-65553 | mV | 1 | Input (FC04) | UINT16
205 | 1 | Min Cell V | 0-65553 | mV | 1 | Input (FC04) | UINT16
206 | 1 | Max chargeable | 0-65553 | A | 100 | Input (FC04) | UINT16
207 | 1 | Max dischargeable | 0-65553 | A | 100 | Input (FC04) | UINT16
208 | 1 | Highest temp cell no# | Ext | 0-65553 | - | Input (FC04) | UINT16
209 | 1 | Lowest temp cell no# | Ext | 0-65553 | - | Input (FC04) | UINT16
210 | 1 | Highest volt cell no# | Ext | 0-65553 | - | Input (FC04) | UINT16
211 | 1 | Lowest volt cell no# | Ext | 0-65553 | - | Input (FC04) | UINT16
212 | 2 | BMS 0 Serial number | - | - | - | Input (FC04) | UINT32 | 0x60
214 | 1 | BMS 0 Firmware version | 0-65553 | - | - | Input (FC04) | UINT16
215 | 1 | BMS 0 model type | 0-65553 | - | - | Input (FC04) | UINT16 | 0x43 = Commercial Product, 0x52 = Residential Product
216 | 1 | BMS 0 FW release | 0-65553 | - | - | Input (FC04) | UINT16
217 | 2 | BMS 1 Serial number | - | - | - | Input (FC04) | UINT32 | 0x01
219 | 1 | BMS 1 Firmware version | 0-65553 | - | - | Input (FC04) | UINT16
220 | 1 | BMS 1 model type | 0-65553 | - | - | Input (FC04) | UINT16 | 0x43 = Commercial Product, 0x52 = Residential Product
221 | 1 | BMS 1 FW release | 0-65553 | - | - | Input (FC04) | UINT16
222 | 2 | BMS 2 Serial number | - | - | - | Input (FC04) | UINT32 | 0x02
224 | 1 | BMS 2 Firmware version | 0-65553 | - | - | Input (FC04) | UINT16
225 | 1 | BMS 2 model type | 0-65553 | - | - | Input (FC04) | UINT16 | 0x43 = Commercial Product, 0x52 = Residential Product
226 | 1 | BMS 2 FW release | 0-65553 | - | - | Input (FC04) | UINT16
227 | 2 | BMS 3 Serial number | - | - | - | Input (FC04) | UINT32 | 0x03
229 | 1 | BMS 3 Firmware version | 0-65553 | - | - | Input (FC04) | UINT16
230 | 1 | BMS 3 model type | 0-65553 | - | - | Input (FC04) | UINT16 | 0x43 = Commercial Product, 0x52 = Residential Product
231 | 1 | BMS 3 FW release | 0-65553 | - | - | Input (FC04) | UINT16
232 | 2 | BMS 4 Serial number | - | - | - | Input (FC04) | UINT32 | 0x04
234 | 1 | BMS 4 Firmware version | 0-65553 | - | - | Input (FC04) | UINT16
235 | 1 | BMS 4 model type | 0-65553 | - | - | Input (FC04) | UINT16 | 0x43 = Commercial Product, 0x52 = Residential Product
236 | 1 | BMS 4 FW release | 0-65553 | - | - | Input (FC04) | UINT16
|  | String 1 | [5 empty] | String IDs = 0x61, 0x11,0x12,0x13,0x14
Modbus Address | Word count | Signal Name | Valid Range | Unit | Scaling | Register Type | Datatype | Description
300 | 1 | Total voltage | 0-65553 | V | 10 | Input (FC04) | UINT16
301 | 1 | Current | "-32768...32767" | - | 100 | Input (FC04) | INT16
302 | 1 | Max temp | "-32768...32767" | °C | 10 | Input (FC04) | INT16
303 | 1 | Min temp | "-32768...32767" | °C | 10 | Input (FC04) | INT16
304 | 1 | Max Cell V | 0-65553 | mV | 1 | Input (FC04) | UINT16
305 | 1 | Min Cell V | 0-65553 | mV | 1 | Input (FC04) | UINT16
306 | 1 | Max chargeable | 0-65553 | A | 100 | Input (FC04) | UINT16
307 | 1 | Max dischargeable | 0-65553 | A | 100 | Input (FC04) | UINT16
308 | 1 | Highest temp cell no# | Ext | 0-65553 | - | Input (FC04) | UINT16
309 | 1 | Lowest temp cell no# | Ext | 0-65553 | - | Input (FC04) | UINT16
310 | 1 | Highest volt cell no# | Ext | 0-65553 | - | Input (FC04) | UINT16
311 | 1 | Lowest volt cell no# | Ext | 0-65553 | - | Input (FC04) | UINT16
312 | 2 | BMS 0 Serial number | - | - | - | Input (FC04) | UINT32 | 0x61
314 | 1 | BMS 0 Firmware version | 0-65553 | - | - | Input (FC04) | UINT16
315 | 1 | BMS 0 model type | 0-65553 | - | - | Input (FC04) | UINT16 | 0x43 = Commercial Product, 0x52 = Residential Product
316 | 1 | BMS 0 FW release | 0-65553 | - | - | Input (FC04) | UINT16
317 | 2 | BMS 1 Serial number | - | - | - | Input (FC04) | UINT32 | 0x11
319 | 1 | BMS 1 Firmware version | 0-65553 | - | - | Input (FC04) | UINT16
320 | 1 | BMS 1 model type | 0-65553 | - | - | Input (FC04) | UINT16 | 0x43 = Commercial Product, 0x52 = Residential Product
321 | 1 | BMS 1 FW release | 0-65553 | - | - | Input (FC04) | UINT16
322 | 2 | BMS 2 Serial number | - | - | - | Input (FC04) | UINT32 | 0x12
324 | 1 | BMS 2 Firmware version | 0-65553 | - | - | Input (FC04) | UINT16
325 | 1 | BMS 2 model type | 0-65553 | - | - | Input (FC04) | UINT16 | 0x43 = Commercial Product, 0x52 = Residential Product
326 | 1 | BMS 2 FW release | 0-65553 | - | - | Input (FC04) | UINT16
327 | 2 | BMS 3 Serial number | - | - | - | Input (FC04) | UINT32 | 0x13
329 | 1 | BMS 3 Firmware version | 0-65553 | - | - | Input (FC04) | UINT16
330 | 1 | BMS 3 model type | 0-65553 | - | - | Input (FC04) | UINT16 | 0x43 = Commercial Product, 0x52 = Residential Product
331 | 1 | BMS 3 FW release | 0-65553 | - | - | Input (FC04) | UINT16
332 | 2 | BMS 4 Serial number | - | - | - | Input (FC04) | UINT32 | 0x14
334 | 1 | BMS 4 Firmware version | 0-65553 | - | - | Input (FC04) | UINT16
335 | 1 | BMS 4 model type | 0-65553 | - | - | Input (FC04) | UINT16 | 0x43 = Commercial Product, 0x52 = Residential Product
336 | 1 | BMS 4 FW release | 0-65553 | - | - | Input (FC04) | UINT16
|  | String 2 | [5 empty] | String IDs = 0x62, 0x21,0x22,0x23,0x24
Modbus Address | Word count | Signal Name | Valid Range | Unit | Scaling | Register Type | Datatype | Description
400 | 1 | Total voltage | 0-65553 | V | 10 | Input (FC04) | UINT16
401 | 1 | Current | "-32768...32767" | - | 100 | Input (FC04) | INT16
402 | 1 | Max temp | "-32768...32767" | °C | 10 | Input (FC04) | INT16
403 | 1 | Min temp | "-32768...32767" | °C | 10 | Input (FC04) | INT16
404 | 1 | Max Cell V | 0-65553 | mV | 1 | Input (FC04) | UINT16
405 | 1 | Min Cell V | 0-65553 | mV | 1 | Input (FC04) | UINT16
406 | 1 | Max chargeable | 0-65553 | A | 100 | Input (FC04) | UINT16
407 | 1 | Max dischargeable | 0-65553 | A | 100 | Input (FC04) | UINT16
408 | 1 | Highest temp cell no# | Ext | 0-65553 | - | Input (FC04) | UINT16
409 | 1 | Lowest temp cell no# | Ext | 0-65553 | - | Input (FC04) | UINT16
410 | 1 | Highest volt cell no# | Ext | 0-65553 | - | Input (FC04) | UINT16
411 | 1 | Lowest volt cell no# | Ext | 0-65553 | - | Input (FC04) | UINT16
412 | 2 | BMS 0 Serial number | - | - | - | Input (FC04) | UINT32 | 0x62
414 | 1 | BMS 0 Firmware version | 0-65553 | - | - | Input (FC04) | UINT16
415 | 1 | BMS 0 model type | 0-65553 | - | - | Input (FC04) | UINT16 | 0x43 = Commercial Product, 0x52 = Residential Product
416 | 1 | BMS 0 FW release | 0-65553 | - | - | Input (FC04) | UINT16
417 | 2 | BMS 1 Serial number | - | - | - | Input (FC04) | UINT32 | 0x21
419 | 1 | BMS 1 Firmware version | 0-65553 | - | - | Input (FC04) | UINT16
420 | 1 | BMS 1 model type | 0-65553 | - | - | Input (FC04) | UINT16 | 0x43 = Commercial Product, 0x52 = Residential Product
421 | 1 | BMS 1 FW release | 0-65553 | - | - | Input (FC04) | UINT16
422 | 2 | BMS 2 Serial number | - | - | - | Input (FC04) | UINT32 | 0x22
424 | 1 | BMS 2 Firmware version | 0-65553 | - | - | Input (FC04) | UINT16
425 | 1 | BMS 2 model type | 0-65553 | - | - | Input (FC04) | UINT16 | 0x43 = Commercial Product, 0x52 = Residential Product
426 | 1 | BMS 2 FW release | 0-65553 | - | - | Input (FC04) | UINT16
427 | 2 | BMS 3 Serial number | - | - | - | Input (FC04) | UINT32 | 0x23
429 | 1 | BMS 3 Firmware version | 0-65553 | - | - | Input (FC04) | UINT16
430 | 1 | BMS 3 model type | 0-65553 | - | - | Input (FC04) | UINT16 | 0x43 = Commercial Product, 0x52 = Residential Product
431 | 1 | BMS 3 FW release | 0-65553 | - | - | Input (FC04) | UINT16
432 | 2 | BMS 4 Serial number | - | - | - | Input (FC04) | UINT32 | 0x24
434 | 1 | BMS 4 Firmware version | 0-65553 | - | - | Input (FC04) | UINT16
435 | 1 | BMS 4 model type | 0-65553 | - | - | Input (FC04) | UINT16 | 0x43 = Commercial Product, 0x52 = Residential Product
436 | 1 | BMS 4 FW release | 0-65553 | - | - | Input (FC04) | UINT16
PCS detailed data
Modbus Address | Word count | Signal Name | Valid Range | Unit | Scaling | Register Type | Datatype | Description
500 | 1 | Active alarm 0 | 0-500 | - | - | Input (FC04) | UINT16 | Nodebit number of active alarm. 0=no alarm
501 | 1 | Active alarm 1 | 0-500 | - | - | Input (FC04) | UINT16
502 | 1 | Active alarm 2 | 0-500 | - | - | Input (FC04) | UINT16
503 | 1 | Active alarm 3 | 0-500 | - | - | Input (FC04) | UINT16
504 | 1 | Input voltage L-N PH1 | 0-65553 | V | 10 | Input (FC04) | UINT16
505 | 1 | Input voltage L-N PH2 | 0-65553 | V | 10 | Input (FC04) | UINT16
506 | 1 | Input voltage L-N PH3 | 0-65553 | V | 10 | Input (FC04) | UINT16
507 | 1 | Input current PH1 | "-32768...32767" | A | 100 | Input (FC04) | INT16
508 | 1 | Input current PH2 | "-32768...32767" | A | 100 | Input (FC04) | INT16
509 | 1 | Input current PH3 | "-32768...32767" | A | 100 | Input (FC04) | INT16
510 | 1 | Input PF PH1 | "-32768...32767" |  | 100 | Input (FC04) | UINT16
511 | 1 | Input PF PH2 | "-32768...32767" |  | 100 | Input (FC04) | UINT16
512 | 2 | Input PF PH3 | "-32768...32767" |  | 100 | Input (FC04) | UINT16
514 | 1 | Output voltage L-N PH1 | 0-65553 | V | 10 | Input (FC04) | UINT16
515 | 1 | Output voltage L-N PH2 | 0-65553 | V | 10 | Input (FC04) | UINT16
516 | 1 | Output voltage L-N PH3 | 0-65553 | V | 10 | Input (FC04) | UINT16
517 | 2 | Output current PH1 | "-32768...32767" | A | 100 | Input (FC04) | INT16
519 | 1 | Output current PH2 | "-32768...32767" | A | 100 | Input (FC04) | INT16
520 | 1 | Output current PH3 | "-32768...32767" | A | 100 | Input (FC04) | INT16
521 | 1 | Battery voltage | 0-65553 | V | 10 | Input (FC04) | UINT16
522 | 1 | Battery current | "-32768...32767" | A | 100 | Input (FC04) | INT16
523 | 2 | CSB APP version | 0-65553 |  | 1 | Input (FC04) | UINT32 | 1st Byte = Major, 2nd byte = Minor, 3rd+4th bytes = build
525 | 2 | MCU APP version | 0-65553 |  | 1 | Input (FC04) | UINT32 | 1st Byte = Major, 2nd byte = Minor, 3rd+4th bytes = build
527 | 2 | UPM1 APP version | 0-65553 |  | 1 | Input (FC04) | UINT32 | 1st Byte = Major, 2nd byte = Minor, 3rd+4th bytes = build
529 | 2 | UPM2 APP version | 0-65553 |  | 1 | Input (FC04) | UINT32 | 1st Byte = Major, 2nd byte = Minor, 3rd+4th bytes = build
531 | 10 | PCS Serial No | 0-65553 |  | 1 | Input (FC04) | String | 20bytes in ASCII
#1
Command ID# | Description
100 | GRID-TIE Go / Stay grid-tied. When system is grid-tied you can send power setpoints.
346 | AUTONOMOUS Go / Stay to autonomous mode
175 | ISLAND Go / Stay to islanding mode
358 | STARTUP Startup system
0 | OFF Shutdown system.
#2
Status ID# | Description
100 | GRID-TIE System is synchronised to AC grid and ready to receive power setpoints
346 | AUTONOMOUS AC grid unavailable, but system up and ready to provide backup power
175 | ISLAND System providing backup power
157 | FAULT System shutdown and in error
358 | STARTUP System starting up, will go grid tied when startup step is finished
245 | SERVICE Service mode active. Modbus commands will be ignored and system can be in any state.
0 | OFF System shutdown. Isssue a startup command to start it up.
#3
Bit offset | Description
0 | Unused
1 | EVENT_GENERAL_DANGER Critical over temperature or over voltage. Immediate inspection needed.
2 | EVENT_GENERAL_ESS_ALARM Alarm conditions. System is probably not working.
3 | EVENT_GENERAL_BATTERY_ALARM
4 | EVENT_GENERAL_PCS_ALARM
5 | EVENT_GENERAL_COMMUNICATION_ALARM
6 | EVENT_GENERAL_ESS_FAULT Fault conditions. System is maybe not working
7 | EVENT_GENERAL_BATTERY_FAULT
8 | EVENT_GENERAL_PCS_FAULT
9 | EVENT_GENERAL_COMMUNICATION_FAULT
10 | EVENT_GENERAL_ESS_WARNING Anormal conditions, but system still fully operationnal for now
11 | EVENT_GENERAL_BATTERY_WARNING
12 | EVENT_GENERAL_USER_ALARM User configurable events
13 | EVENT_GENERAL_USER_FAULT User configurable events
14 | EVENT_GENERAL_USER_WARNING User configurable events
15 | EVENT_GENERAL_USER_NOTICE User configurable events
#4
Error ID# | Description
0 | No fault condition / not acked error event
1 | GENERAL_DANGER Critical over temperature or over voltage. Immediate inspection needed.
199 | GENERAL_ESS_ALARM Alarm conditions. System is probably not working.
200 | GENERAL_BATTERY_ALARM
300 | GENERAL_PCS_ALARM
400 | GENERAL_COMMUNICATION_ALARM
1199 | GENERAL_ESS_FAULT Fault conditions. System is maybe not working
1200 | GENERAL_BATTERY_FAULT
1300 | GENERAL_PCS_FAULT
1400 | GENERAL_COMMUNICATION_FAULT
2099 | GENERAL_ESS_WARNING Anormal conditions, but system still fully operationnal for now
2200 | GENERAL_BATTERY_WARNING