## Modbus_Interface
Interfacing xStorage System Controller
Protocol: Modbus TCP
Ext Modbus Master #1, EATON Modbus Slave
Connection to xStorage System Controller Ethernet Port #1
The stated interface is per Energy Storage System (ESS, i.e. system controller + inverter + batteries)
Preference that whole block is sent cyclically, >=500ms from Ext
All data is big-endian
Mode | No. | Signal Name | Logical Direction |  | Valid Range | Unit | Scaling | Register Type | Datatype | Modbus Address | Description
|  |  | Source | Destination
Slave (Modbus) | 1 | System Status | Ext | ESS | 0-1000 | - | - | Holding (FC03) | UINT16 | 0 | Command ID# Description 100 GRID-TIE Go / Stay grid-tied. When system is grid-tied you can send power setpoints. 346 AUTONOMOUS Go / Stay to autonomous mode 175 ISLAND Go / Stay to islanding mode 358 STARTUP Startup system 0 OFF Shutdown system.
Slave (Modbus) | 2 | Power Request (active Power) (Big-Endian) | Ext | ESS | -1000000…1000000 | W | 1 | Holding (FC03) | INT32 | 1 | Power setpoint. By default, positive is discharging and negative charging.
Slave (Modbus) | 4 | Power Request (reactive Power) (Big-Endian) | Ext | ESS | -1000000…1000000 | Var | 1 | Holding (FC03) | INT32 | 3 | (not implemented)
Slave (Modbus) | 6 | Ext Error | Ext | ESS | 0=no Error, 1=Error | - | - | Holding (FC03) | UINT16 | 5 | Error in external contol unit. Not used for now - you can write what you want into this register.
Slave (Modbus) | 7 | General Error Reset | Ext | ESS | trigger on flank | - | - | Holding (FC03) | UINT16 | 6 | Error reset of ESS error. Writing 1 into this register will ack the current "Storage System Error", possibly displaying a new one or eventually the same if same fault condition is still present/occurs again.
Slave (Modbus) | 8 | Alive Counter | Ext | ESS | 0-65553 | - | - | Holding (FC03) | UINT16 | 7 | Alive value, upcounting, to check if connection is alive, counting up until 65535 and restarts with 0. If you choose to write something into this register, writing at least twice the same value consecutively will start a timeout. If the timeout expires, the system will be put into idle. Writing another new value will stop and reset it.
If no write request is received for a given amount of time (indenpendently of the register / registers ESS writes into) system is put to idle. External controller should write the whole range of the registers at once, at a rate of maximum twice a second.
Mode | No. | Signal Name | Logical Direction |  | Valid Range | Unit |  | Register Type | Datatype | Modbus Address | Description
|  |  | Source | Destination
Slave (Modbus) | 1 | System Status | ESS | Ext | 0-1000 | - | - | Iput (FC04) | UINT16 | 0 | Status ID# Description 100 GRID-TIE System is synchronised to AC grid and ready to receive power setpoints 346 AUTONOMOUS AC grid unavailable, but system up and ready to provide backup power 175 ISLAND System providing backup power 157 FAULT System shutdown and in error 358 STARTUP System starting up, will go grid tied when startup step is finished 245 SERVICE Service mode active. Modbus commands will be ignored and system can be in any state. 0 OFF System shutdown. Isssue a startup command to start it up.
Slave (Modbus) | 5 | Current mesured active power | ESS | Ext | -1000000…1000000 | W | 1 | Iput (FC04) | INT32 | 4
Slave (Modbus) | 7 | Current measured reactive power | ESS | Ext | -1000000…1000000 | Var | 1 | Iput (FC04) | INT32 | 6
Slave (Modbus) | 9 | State of Charge | ESS | Ext | 0…100 | 1% | 1 | Iput (FC04) | UINT8 | 8
Slave (Modbus) | 10 | Alive Counter | ESS | Ext | 0-65553 | - | - | Iput (FC04) | UINT16 | 9 | Alive value, upcounting, for Ext to check if connection is alive, counting up until 65535 and restarts with 0. System uses two separate counters (Ext increases own counter, ESS increases own counter)
Slave (Modbus) | 11 | Maximum available power charge | ESS | Ext | 0…10000000 | W | 1 | Iput (FC04) | INT32 | 10 | Maximum charging power capability. Reference point at inverter AC terminals
Slave (Modbus) | 13 | Maximum available power discharge | ESS | Ext | 0…10000000 | W | 1 | Iput (FC04) | INT32 | 12 | Maximum discharging power capability. Reference point at inverter AC terminals
Slave (Modbus) | 15 | Storage System Error | ESS | Ext | Error Code | - | - | Iput (FC04) | UINT16 | 14 | Error ID# Description 0 No fault condition / not acked error event 1 GENERAL_DANGER Critical over temperature or over voltage. Immediate inspection needed. 199 GENERAL_ESS_ALARM Alarm conditions. System is probably not working. 200 GENERAL_BATTERY_ALARM 300 GENERAL_PCS_ALARM 400 GENERAL_COMMUNICATION_ALARM 1199 GENERAL_ESS_FAULT Fault conditions. System is maybe not working 1200 GENERAL_BATTERY_FAULT 1300 GENERAL_PCS_FAULT 1400 GENERAL_COMMUNICATION_FAULT 2099 GENERAL_ESS_WARNING Anormal conditions, but system still fully operationnal for now 2200 GENERAL_BATTERY_WARNING
Slave (Modbus) | 16 | Battery bank capacity | ESS | Ext | 0....100E6 | Wh | 1 | Iput (FC04) | UINT32 | 15 | Energy in battery (last 3 digits insignificant)
Slave (Modbus) | 18 | Energy available to discharge (total availale energy) | ESS | Ext | 0....100E6 | Wh | 1 | Iput (FC04) | UINT32 | 17 | Value given at full (rated) system power
Slave (Modbus) | 20 | Energy available to charge (total available energy) | ESS | Ext | 0....100E6 | Wh | 1 | Iput (FC04) | UINT32 | 19 | Value given at full (rated) system power
Slave (Modbus) | 22 | Discharging energy reserved for other users | ESS | Ext | 0....100E6 | Wh | 1 | Iput (FC04) | UINT32 | 21 | Value given at full (rated) system power
Slave (Modbus) | 24 | Charging energy reserved for other users | ESS | Ext | 0....100E6 | Wh | 1 | Iput (FC04) | UINT32 | 23 | Value given at full (rated) system power
Slave (Modbus) | 26 | Unique ID | ESS | Ext | - | - | - | Iput (FC04) | String(64) | 25 | XXX-NN-nnnnnnnn (Site ID - number - PCS serial number)
Slave (Modbus) | 58 | Battery bank voltage (average voltage of all connected strings) | ESS | Ext | 0-65553 | V | 10 | Iput (FC04) | UINT16 | 57
Slave (Modbus) | 59 | Maximum cell voltage of the present strings | ESS | Ext | 0-65553 | mV | 1 | Iput (FC04) | UINT16 | 58
Slave (Modbus) | 60 | Minimum cell voltage of the present strings | ESS | Ext | 0-65553 | mV | 1 | Iput (FC04) | UINT16 | 59
Slave (Modbus) | 61 | ID of the string with max cell voltage | ESS | Ext | 0-65553 | - | - | Iput (FC04) | UINT16 | 60
Slave (Modbus) | 62 | ID of the string with min cell voltage | ESS | Ext | 0-65553 | - | - | Iput (FC04) | UINT16 | 61
Slave (Modbus) | 63 | ID of the pack with max cell voltage | ESS | Ext | 0-65553 | - | - | Iput (FC04) | UINT16 | 62
Slave (Modbus) | 64 | ID of the pack with min cell voltage | ESS | Ext | 0-65553 | - | - | Iput (FC04) | UINT16 | 63
Slave (Modbus) | 65 | Maximum cell temperature of the present strings | ESS | Ext | "-32768...32767" | °C | 10 | Iput (FC04) | INT16 | 64
Slave (Modbus) | 66 | Minimum cell temperature of the present strings | ESS | Ext | "-32768...32767" | °C | 10 | Iput (FC04) | INT16 | 65
Slave (Modbus) | 67 | ID of the string with max cell temp | ESS | Ext | 0-65553 | - | - | Iput (FC04) | UINT16 | 66
Slave (Modbus) | 68 | ID of the string with min cell temp | ESS | Ext | 0-65553 | - | - | Iput (FC04) | UINT16 | 67
Slave (Modbus) | 69 | ID of the pack with max cell temp | ESS | Ext | 0-65553 | - | - | Iput (FC04) | UINT16 | 68
Slave (Modbus) | 70 | ID of the pack with min cell temp | ESS | Ext | 0-65553 | - | - | Iput (FC04) | UINT16 | 69
Slave (Modbus) | 71 | Minimum current of the connected strings | ESS | Ext | 0-65553 | A | 100 | Iput (FC04) | UINT16 | 70
Slave (Modbus) | 72 | Maximum current of the connected strings | ESS | Ext | 0-65553 | A | 100 | Iput (FC04) | UINT16 | 71
Slave (Modbus) | 73 | ID of the string with the minimum current | ESS | Ext | 0-65553 | - | - | Iput (FC04) | UINT16 | 72
Slave (Modbus) | 74 | ID of the string with the maximum current | ESS | Ext | 0-65553 | - | - | Iput (FC04) | UINT16 | 73
Slave (Modbus) | 75 | Minimum chargeable current of the connected strings | ESS | Ext | 0-65553 | A | 100 | Iput (FC04) | UINT16 | 74
Slave (Modbus) | 76 | Maximum chargeable current of the connected strings | ESS | Ext | 0-65553 | A | 100 | Iput (FC04) | UINT16 | 75
Slave (Modbus) | 77 | ID of the string with the minimum chargeable current | ESS | Ext | 0-65553 | - | - | Iput (FC04) | UINT16 | 76
Slave (Modbus) | 78 | ID of the string with the maximum chargeable current | ESS | Ext | 0-65553 | - | - | Iput (FC04) | UINT16 | 77
Slave (Modbus) | 79 | Actual set converter power (with regulation if enabled) | ESS | Ext | -1000000…1000000 | W | 1 | Iput (FC04) | INT32 | 78
Slave (Modbus) | 81 | Grid frequency | ESS | Ext | 0-65553 | Hz | 100 | Iput (FC04) | UINT16 | 80
Slave (Modbus) | 82 | Converter ambiant temperature | ESS | Ext | 0-65553 | °C | 10 | Iput (FC04) | UINT16 | 81
Slave (Modbus) | 83 | Amount of strings configured | ESS | Ext | 1…54 | - | - | Iput (FC04) | UINT16 | 82
Slave (Modbus) | 84 | Status of string 0 | ESS | Ext | 0...3 | - | - | Iput (FC04) | UINT16 | 83 | 0 = OFFLINE, 1= DETECTING, 2= AVAILABLE, 3= ONLINE
Slave (Modbus) | 85 | Status of string 1 | ESS | Ext | 0...3 | - | - | Iput (FC04) | UINT16 | 84 | 0 = OFFLINE, 1= DETECTING, 2= AVAILABLE, 3= ONLINE
Slave (Modbus) | 86 | Status of string 2 | ESS | Ext | 0...3 | - | - | Iput (FC04) | UINT16 | 85 | 0 = OFFLINE, 1= DETECTING, 2= AVAILABLE, 3= ONLINE
Slave (Modbus) | 87 | Status of string 3 | ESS | Ext | 0...3 | - | - | Iput (FC04) | UINT16 | 86 | 0 = OFFLINE, 1= DETECTING, 2= AVAILABLE, 3= ONLINE
Slave (Modbus) | 88 | Status of string 4 | ESS | Ext | 0...3 | - | - | Iput (FC04) | UINT16 | 87 | 0 = OFFLINE, 1= DETECTING, 2= AVAILABLE, 3= ONLINE
Slave (Modbus) | 89 | Status of string 5 | ESS | Ext | 0...3 | - | - | Iput (FC04) | UINT16 | 88 | 0 = OFFLINE, 1= DETECTING, 2= AVAILABLE, 3= ONLINE
Slave (Modbus) | 90 | Status of string 6 | ESS | Ext | 0...3 | - | - | Iput (FC04) | UINT16 | 89 | 0 = OFFLINE, 1= DETECTING, 2= AVAILABLE, 3= ONLINE
Slave (Modbus) | 91 | Status of string 7 | ESS | Ext | 0...3 | - | - | Iput (FC04) | UINT16 | 90 | 0 = OFFLINE, 1= DETECTING, 2= AVAILABLE, 3= ONLINE
Slave (Modbus) | 92 | Status of string 8 | ESS | Ext | 0...3 | - | - | Iput (FC04) | UINT16 | 91 | 0 = OFFLINE, 1= DETECTING, 2= AVAILABLE, 3= ONLINE
Slave (Modbus) | 93 | Status of string 9 | ESS | Ext | 0...3 | - | - | Iput (FC04) | UINT16 | 92 | 0 = OFFLINE, 1= DETECTING, 2= AVAILABLE, 3= ONLINE
Slave (Modbus) | 94 | Status of string 10 | ESS | Ext | 0...3 | - | - | Iput (FC04) | UINT16 | 93 | 0 = OFFLINE, 1= DETECTING, 2= AVAILABLE, 3= ONLINE
Slave (Modbus) | 95 | Status of string 11 | ESS | Ext | 0...3 | - | - | Iput (FC04) | UINT16 | 94 | 0 = OFFLINE, 1= DETECTING, 2= AVAILABLE, 3= ONLINE
Slave (Modbus) | 96 | Status of string 12 | ESS | Ext | 0...3 | - | - | Iput (FC04) | UINT16 | 95 | 0 = OFFLINE, 1= DETECTING, 2= AVAILABLE, 3= ONLINE
Slave (Modbus) | 97 | Status of string 13 | ESS | Ext | 0...3 | - | - | Iput (FC04) | UINT16 | 96 | 0 = OFFLINE, 1= DETECTING, 2= AVAILABLE, 3= ONLINE
Slave (Modbus) | 98 | Status of string 14 | ESS | Ext | 0...3 | - | - | Iput (FC04) | UINT16 | 97 | 0 = OFFLINE, 1= DETECTING, 2= AVAILABLE, 3= ONLINE
Slave (Modbus) | 99 | Status of string 15 | ESS | Ext | 0...3 | - | - | Iput (FC04) | UINT16 | 98 | 0 = OFFLINE, 1= DETECTING, 2= AVAILABLE, 3= ONLINE
Slave (Modbus) | 100 | Status of string 16 | ESS | Ext | 0...3 | - | - | Iput (FC04) | UINT16 | 99 | 0 = OFFLINE, 1= DETECTING, 2= AVAILABLE, 3= ONLINE
Slave (Modbus) | 101 | Status of string 17 | ESS | Ext | 0...3 | - | - | Iput (FC04) | UINT16 | 100 | 0 = OFFLINE, 1= DETECTING, 2= AVAILABLE, 3= ONLINE
Slave (Modbus) | 102 | Status of string 18 | ESS | Ext | 0...3 | - | - | Iput (FC04) | UINT16 | 101 | 0 = OFFLINE, 1= DETECTING, 2= AVAILABLE, 3= ONLINE
Slave (Modbus) | 103 | Status of string 19 | ESS | Ext | 0...3 | - | - | Iput (FC04) | UINT16 | 102 | 0 = OFFLINE, 1= DETECTING, 2= AVAILABLE, 3= ONLINE
Slave (Modbus) | 104 | Status of string 20 | ESS | Ext | 0...3 | - | - | Iput (FC04) | UINT16 | 103 | 0 = OFFLINE, 1= DETECTING, 2= AVAILABLE, 3= ONLINE
Slave (Modbus) | 105 | Status of string 21 | ESS | Ext | 0...3 | - | - | Iput (FC04) | UINT16 | 104 | 0 = OFFLINE, 1= DETECTING, 2= AVAILABLE, 3= ONLINE
Slave (Modbus) | 106 | Status of string 22 | ESS | Ext | 0...3 | - | - | Iput (FC04) | UINT16 | 105 | 0 = OFFLINE, 1= DETECTING, 2= AVAILABLE, 3= ONLINE
Slave (Modbus) | 107 | Status of string 23 | ESS | Ext | 0...3 | - | - | Iput (FC04) | UINT16 | 106 | 0 = OFFLINE, 1= DETECTING, 2= AVAILABLE, 3= ONLINE
Slave (Modbus) | 108 | Status of string 24 | ESS | Ext | 0...3 | - | - | Iput (FC04) | UINT16 | 107 | 0 = OFFLINE, 1= DETECTING, 2= AVAILABLE, 3= ONLINE
Slave (Modbus) | 109 | Status of string 25 | ESS | Ext | 0...3 | - | - | Iput (FC04) | UINT16 | 108 | 0 = OFFLINE, 1= DETECTING, 2= AVAILABLE, 3= ONLINE
Slave (Modbus) | 110 | Status of string 26 | ESS | Ext | 0...3 | - | - | Iput (FC04) | UINT16 | 109 | 0 = OFFLINE, 1= DETECTING, 2= AVAILABLE, 3= ONLINE
Slave (Modbus) | 111 | Status of string 27 | ESS | Ext | 0...3 | - | - | Iput (FC04) | UINT16 | 110 | 0 = OFFLINE, 1= DETECTING, 2= AVAILABLE, 3= ONLINE
Slave (Modbus) | 112 | Status of string 28 | ESS | Ext | 0...3 | - | - | Iput (FC04) | UINT16 | 111 | 0 = OFFLINE, 1= DETECTING, 2= AVAILABLE, 3= ONLINE
Slave (Modbus) | 113 | Status of string 29 | ESS | Ext | 0...3 | - | - | Iput (FC04) | UINT16 | 112 | 0 = OFFLINE, 1= DETECTING, 2= AVAILABLE, 3= ONLINE
Slave (Modbus) | 114 | Status of string 30 | ESS | Ext | 0...3 | - | - | Iput (FC04) | UINT16 | 113 | 0 = OFFLINE, 1= DETECTING, 2= AVAILABLE, 3= ONLINE
Slave (Modbus) | 115 | Status of string 31 | ESS | Ext | 0...3 | - | - | Iput (FC04) | UINT16 | 114 | 0 = OFFLINE, 1= DETECTING, 2= AVAILABLE, 3= ONLINE
Slave (Modbus) | 116 | Status of string 32 | ESS | Ext | 0...3 | - | - | Iput (FC04) | UINT16 | 115 | 0 = OFFLINE, 1= DETECTING, 2= AVAILABLE, 3= ONLINE
Slave (Modbus) | 117 | Status of string 33 | ESS | Ext | 0...3 | - | - | Iput (FC04) | UINT16 | 116 | 0 = OFFLINE, 1= DETECTING, 2= AVAILABLE, 3= ONLINE
Slave (Modbus) | 118 | Status of string 34 | ESS | Ext | 0...3 | - | - | Iput (FC04) | UINT16 | 117 | 0 = OFFLINE, 1= DETECTING, 2= AVAILABLE, 3= ONLINE
Slave (Modbus) | 119 | Status of string 35 | ESS | Ext | 0...3 | - | - | Iput (FC04) | UINT16 | 118 | 0 = OFFLINE, 1= DETECTING, 2= AVAILABLE, 3= ONLINE
Slave (Modbus) | 120 | Status of string 36 | ESS | Ext | 0...3 | - | - | Iput (FC04) | UINT16 | 119 | 0 = OFFLINE, 1= DETECTING, 2= AVAILABLE, 3= ONLINE
Slave (Modbus) | 121 | Status of string 37 | ESS | Ext | 0...3 | - | - | Iput (FC04) | UINT16 | 120 | 0 = OFFLINE, 1= DETECTING, 2= AVAILABLE, 3= ONLINE
Slave (Modbus) | 122 | Status of string 38 | ESS | Ext | 0...3 | - | - | Iput (FC04) | UINT16 | 121 | 0 = OFFLINE, 1= DETECTING, 2= AVAILABLE, 3= ONLINE
Slave (Modbus) | 123 | Status of string 39 | ESS | Ext | 0...3 | - | - | Iput (FC04) | UINT16 | 122 | 0 = OFFLINE, 1= DETECTING, 2= AVAILABLE, 3= ONLINE
Slave (Modbus) | 124 | Status of string 40 | ESS | Ext | 0...3 | - | - | Iput (FC04) | UINT16 | 123 | 0 = OFFLINE, 1= DETECTING, 2= AVAILABLE, 3= ONLINE
Slave (Modbus) | 125 | Status of string 41 | ESS | Ext | 0...3 | - | - | Iput (FC04) | UINT16 | 124 | 0 = OFFLINE, 1= DETECTING, 2= AVAILABLE, 3= ONLINE
Slave (Modbus) | 126 | Status of string 42 | ESS | Ext | 0...3 | - | - | Iput (FC04) | UINT16 | 125 | 0 = OFFLINE, 1= DETECTING, 2= AVAILABLE, 3= ONLINE
Slave (Modbus) | 127 | Status of string 43 | ESS | Ext | 0...3 | - | - | Iput (FC04) | UINT16 | 126 | 0 = OFFLINE, 1= DETECTING, 2= AVAILABLE, 3= ONLINE
Slave (Modbus) | 128 | Status of string 44 | ESS | Ext | 0...3 | - | - | Iput (FC04) | UINT16 | 127 | 0 = OFFLINE, 1= DETECTING, 2= AVAILABLE, 3= ONLINE
Slave (Modbus) | 129 | Status of string 45 | ESS | Ext | 0...3 | - | - | Iput (FC04) | UINT16 | 128 | 0 = OFFLINE, 1= DETECTING, 2= AVAILABLE, 3= ONLINE
Slave (Modbus) | 130 | Status of string 46 | ESS | Ext | 0...3 | - | - | Iput (FC04) | UINT16 | 129 | 0 = OFFLINE, 1= DETECTING, 2= AVAILABLE, 3= ONLINE
Slave (Modbus) | 131 | Status of string 47 | ESS | Ext | 0...3 | - | - | Iput (FC04) | UINT16 | 130 | 0 = OFFLINE, 1= DETECTING, 2= AVAILABLE, 3= ONLINE
Slave (Modbus) | 132 | Status of string 48 | ESS | Ext | 0...3 | - | - | Iput (FC04) | UINT16 | 131 | 0 = OFFLINE, 1= DETECTING, 2= AVAILABLE, 3= ONLINE
Slave (Modbus) | 133 | Status of string 49 | ESS | Ext | 0...3 | - | - | Iput (FC04) | UINT16 | 132 | 0 = OFFLINE, 1= DETECTING, 2= AVAILABLE, 3= ONLINE
Slave (Modbus) | 134 | Status of string 50 | ESS | Ext | 0...3 | - | - | Iput (FC04) | UINT16 | 133 | 0 = OFFLINE, 1= DETECTING, 2= AVAILABLE, 3= ONLINE
Slave (Modbus) | 135 | Status of string 51 | ESS | Ext | 0...3 | - | - | Iput (FC04) | UINT16 | 134 | 0 = OFFLINE, 1= DETECTING, 2= AVAILABLE, 3= ONLINE
Slave (Modbus) | 136 | Status of string 52 | ESS | Ext | 0...3 | - | - | Iput (FC04) | UINT16 | 135 | 0 = OFFLINE, 1= DETECTING, 2= AVAILABLE, 3= ONLINE
Slave (Modbus) | 137 | Status of string 53 | ESS | Ext | 0...3 | - | - | Iput (FC04) | UINT16 | 136 | 0 = OFFLINE, 1= DETECTING, 2= AVAILABLE, 3= ONLINE